## Heat Pumps
Tammie Requested all HP Makes and Models All Hours had on file.
HP-1: CXO Office | HP-2: Tammie's Office | HP-3: Front Office | HP-4: Front Desk | HP-5: Large Conference Room 1 | HP-6: South East Cubicals | HP-7: South West Cubicals | HP-8: South Conference Room | HP-9: South West Offices | HP-10: N/A | HP-11: North West Cubicals/Tracee office | HP-12: North West Cubicals | HP-13: North West Cubicals | HP-14: North West Offices | HP-15: Break Room | HP-16: Lobby | HP-17: North East IT Area | HP-18: North East Offices/IT Offices | HP-19: Gym/Shawn (per All Hours this one controls Shawn's office, but per our plans it does not) currently doing additional research. | HP-20: this actually controls Shawns from the research I did on our building plans. ALL Hours has not sent us over any info for the HP unit.
Make: Climate Control | Make: Daikin | Make: McQuay | Make: Climate Control | Make: Climate Control | Make: Climate Control | Make: Climate Master | Make: Daikin | Make: Climate Control |  | Make: Climate Control | Make: Climate Control | Make: Climate Control | Make: Water Furnace | Make: McQuay | Make: Climate Control | Make: Daikin | Make: Climate Master | Make: Climate Control
Model: CC260GA | Model: WCCW5030BFYRS01YYACYYY | Model: WCCH2036MFYRS01YYACYYY | Model: CC330GK | Model: CC330GK | Model: CC420GK | Model: TCH042AHC30CRSS | Model: WCCW5042BFYRS01YYA0YYY | Model: CC420GK |  | Model: CC420GK | Model: CC420GK | Model: CC330GK | Model: USH042SR000CBNNA8N00SSD | Model: WCRH1042MFYRS01 | Model: CC330G | Model: VXH036B301CRE2NSA | Model: TCH042AHC30CRSS | Model: CC420GK
Serial: 434180737 | Serial: 669808000 | Serial: 285693400 | Serial: 434280280 | Serial: 434280398 | Serial: 434270382 | Serial: R11511314 | Serial: 669809400 | Serial: 433440776 |  | Serial: 433480472 | Serial: 433440796 | Serial: 434280278 | Serial: 181100880 | Serial: 285696500 | Serial: 434280276 | Serial: VA2148 | Serial: Q13226259 | Serial: 433440815
Year: 2004 | Year: 2020 | Year: 2009 | Year: 2004 | Year: 2004 | Year: 2004 | Year: 2013 | Year: 2020 | Year: 2004 |  | Year: 2004 | Year: 2004 | Year: 2004 | Year: 2018 | Year: 2006 | Year: 2004 | Year: 2009 | Year: 2012 | Year: 2004
Brett Elliott sent Eric an email stating this unit was replaced in July 2020, which does not match the above year info. Possibly that Brett got this unit mixed with Unit #2 that was replaced. TD researched |  |  |  | 8/7/23, i15615 complain HP is not cooling. tested water loop tested freon, the compressor is cold and sweaty, replaced filter, adjusted the refridgerant charge, now runing fine. $2,282.81 (all services this day) |  |  | Brett Elliott sent Eric an email stating this unit was replaced in July 2020, which matches the above year info. TD researched |  | Brett Elliott sent Eric an email stating this unit was replaced in January 2019. But, the tech provided no info on this unit to Tammie when she did her research. |  | 8/7/23, i15615 complain HP complain too warm, this system is part of HP 12, measured discharge air temrp at the diffuser, the hp is operating ok, office is not near the tstat, adjust tstat and recommend adding a tstat for this office, fan is running. |  | Brett Elliott sent Eric an email stating this unit was replaced in January 2019. |  | 8/7/23, i15615 complain HP 16 heat pump is not cooling. compressor is locked out. reset the control board. the compressor started. the blower did not. inspected the blower. the motor is hot and shut down on the internal overload. the capacitor tests bad. I let the motor cool off and replaced the capacitor. started the motor measured motor amps teste the discharge air temp. operating ok now. $2,282.81 (for all services this day) |  |  | 8/7/23, i15615 complain HP 19, the office on the north west side of building is too warm. no tstate in this space. (SHAWN OFFICE) need to replace and add tstat and use a sensor or adjust from gym. 8/8/23, i15582 $122.008/3/23 Contact is Tori 6145127925... No AC in accounting office area Checked in to find out for sure which area/office was having trouble with no AC. Found that the large common area outside the accounting office was cooling well, but the 2 supply registers were not. Lifted ceiling tiles to find those runs are branches from the HP and T'stat in the gym. Showed the office personnel how to adjust that T'stat to their liking in that office. Set up the program to raise nighttime temperature to 76 and daytime to 72 deg. WO complete. Tech already on site for PM. 8/11/23, Q3934, HP 19 sent quote $1,285.00 to install new tstate in Shawns office and wire as needed. (Shawn did not want to move forward with this.) | Tammie Questioned All Hours and they said that Eric told them when we moved in we were not fixing this HP. They said it has never worked.
|  |  | 5/7/24, i18373, Adam L. no a/c 1/2 building reported we were just out for PM. HP 4 the blower was running but not compressor. found board locked out. reset unit and compressor ran with no issues. temp dropped to setpoint within 10 mins. water lines had 10 split. this has been an issue in the past when switching between heating and cooling. $307.00 | 9/18/23, quote q3453, Replace heat pump $9,480.00 (I don't see where this was completed yet) Climate Control Model CC330GK, Serial #43428039 THEY SAID IT WAS RUNNING FINE ABOVE SO I DON'T KNOW WHY THEY SENT A REPLACEMENT QUOTE. | [5 empty] | 1/22/25, i21878, Eric arrived looked in ceiling for a losoe spade on low voltage side. was told tstate went blank yesterday. found loose connections, removed batteries from tstate unit got back to good temp. $747.00 (for all) | [6 empty] | 1/22/25, i21878, Eric arrived Wshp 18 in IT had no call to control board. Found that thermostat is not on the wall all the way attached. Put tstat back in to base, now working. $747.00 (for entire service call) | 1/22/25, i21878, Eric arrived HP 19 in exercise room/ unit had light for lock out on reset unit no issues with temps and amp draws are good.
|  |  | 10/4/24, quote q5240, Replace heat pump $8,560.00 (I don't see where this was completed yet) 2.5 Ton Water Furnace water source heat pump to replace Climate Control Model #CC330GK/Serial #434280260 The serial number is different here than what was provided to me above on 10/29/25, by Adam Nebbergall | 10/4/24, quote q5240, Replace heat pump $8,560.00 (I don't see where this was completed yet) 2.5 Ton Water Furance water source heat pump to replace (mentions conference room) Climate Control Model CC330GK, Serial #434280398 | [5 empty] | 6/11/25, i23814 $492.00, Bryon HP11,tested, reprogrammed thermo, reset the breaker, the unit was in a hard lockout. reset the unit |  | 10/16/25, quote #1311 Replace Water Source Heat Pump #13 $11,620 |  |  | 10/16/25, quote #1310 Replace Water Source Heat Pump #16 $11,798.34

## Issues
Current outstanding issues need addressed 2026.
7/24/25, Alex F came out because ceiling tiles fell down near copier. i24525, $252.00, said the trap was plugged so he removed the trap and drained the condensate pan into a bucket. flushed out the trap and made sure it was clear and also checked the drain to verify it was clear. reset pwer to the unit and replaced the trap.

## Questions
Heat Pumps
2004 | 10*11620=$116,200 | Climate Controls | Confirmed All 2004 Models are Obsolete and parts are more than likely not able to be obtained.
2006 | 1 | Make: McQuay
2009 | 2 | Make: McQuay & Make: Daikin
2012 | 1 | Make Climate Master
2013 | 1 | Make Climate Master
2018 | 1 | Make: Water Furnace
2020 | 2 | Make: Daikin
MISSING INFO | 1 | ??? HP10
MISSING INFO | 1 | ??? HP20

## Tower & Spray Pump
8/8/23, i15261, cooling tower spray pump bearings failed provide and install new spray pump $9,295.00
4/17/25, back flow to cooling tower leaking (outside scope) JR replaced the backflow and submitted results to the city $3,200.00
4/29/25, IER Services (Ohio Plumbing & Boiler Charlie Hautz) provide and install new seal kit, shaft sleeve, motor bearings and volute gasket for spare spray pump, (back up pump for spray tower that was rebuilt)
5/5/25, Invoice i23051 Adam found cooling tower locked up and called Steve out. They said it seized and needed replaced. $362.00 for labor.
5/5/25, IER Services (Ohio Plumbing & Boiler Charlie Hautz) repair broken pvc pipe and free up seized spray pump labor $420 materials $132.05= $552.05 completed | All Hours gave me a quote q6019, 4/21/25, to replace the spray tower pump and labor $13,184.00. Then Tammie asked for just labor and the quote q6025 for that was $3,240.00. I got a quote for just the pump from Elitaire $6,800.36. So went with IER Services
6/19/25, Cooling Tower, quote #q6141, Replace the Float Valve on the tower. (work was completed by Steve) $754.50

## Reg Maint.
Orig contract dated 1/4/22, 30 day written cancelation notice required. | 20 water source heat pumps, 1 cooling tower, 1 boiler, 1 MUA unit, 4 PUMPS, 7 Exhaust Fans
11/29/23, i16423, $1,677.00 prev. maint.
11/4/24 by Seth L. invoiced i20924 on 11/15/24, Preventative Maint. QTR 4th $1,744.08
serviced on 1/10/25 and 1/15/25 by Caleb Ownby 2/6/25, Invoice i21645, QTR 1 Preventative Maint. $1,744.08
5/12/25, i23007, $1,813.84 April Prev. maint. Adam Nebbergall, Eric Deputy. found the backflow in the boiler room was leaking water needs replaced. Adam found cooling tower locked up.
8/29/25, July Prev. Maint. Caleb O. Performed $1,813.84
10/14 & 10/15/25, invoice i 25286, Adam N. mentioned issues with hp #13 * #16 added notes to that tab. $1,813.84

## 4 Inside Pumps
2/13/25, invoice i22141, 2/21/25, Gas valve will not adjust. Provided and installed new gas valve. $1,619.26 Boiler
6/2/25, i23683, $2,750.00 Replaced the Float Switch and found out pump 1 isn't working all the time. But we have a second pump it kicks to. Steve W. John Trimmer, 6225: Tammy is requesting us to come look at her cooling tower. Steve W Contacted by Tammy and advised cooling tower was not working properly. She stated tower was not running, loop temperature over the weekend reached 120°. At this time, contacted Ryan and placed a service call. Arrived onsite and checked in with Tammy. Went to the cooling tower and found the tower was not being called by temperature. First step I did verify spray bar pump was working properly, fan working properly. Next check was to verify we had flow from pumps. Found pump number one motor running, found pressure gauges reading zero acrosstheboard. Added water to system to get pressures where they belong (these are indicated on the dial). Still at this point, it appears I have no flow from building to the tower. Further check by removing suction cover and strainers and found coupler between motor and pump on number one not engaged. Found flow switch had been bypassed, this not allowing secondary pump to engage due to lack of flow. I disconnected flow switch, secondary pump, presently engaged. Cooling tower temperature is now rising, cooling tower fan and spray bar pump are now on. I will investigate and see what needs to be done to correct this situation and have it put back together correctly. 6225 Return to site, found secondary pump tripped on overloads. Went through and saw no reason for this, reset motor and came back online. After finding secondary pump, tripped out, reconnected coupler for pump number one which is the primary pump, primary pump now back online. Flow which still needs to be replaced. Spoke to Tammy and will try to do this end of the week providing we can find the flow switch. Checked out with Tammy. Job not completed 1 $2,750.00 $2,750.00 Tower 7/9/25 John and Caleb Replaced flow switch with new. Removed glycol and pumped back in when valve replacement was complete. Turned so stem back on and reset all units. Job is complete 7/11/25 John Trimmer Returned about loud pump. Upon arrival minimal noise, bled all bleeders and added a little water. Noise dropped a little. Point of contact said noise was better and was happy with results. Job is complete 1 $0.00 $0.00 Tower Labor
NEEDS TO BE FIXED
1st pump down. Tammie has monitored it being bypassed all winter. IER recommends to try to rebuid this pump motor first. Estimate $3,985.23

## Pump above door boiler room
Tammie will have the new PM company get her details on this.

## Backflows
We have 3 backflows
1 inside boiler room ceiling that was replaced 2023-2024 (Tested last by All Hours 2026, and reported to the City of Westerville)
1 inside boiler room back wall that was replaced 2023-2024 (Tested last by All Hours 2026, and reported to the City of Westerville)
1 outside at irrigation system that was replaced 2025 (this one is removed in the winter and brought inside with Rain One winterizes our Irrigation system. Then reinstalled in the Spring when start up of irrigation system. They test this backflow and report it to the City of Westerville.
2/14/25, i21342, Provide and install one backflow preventer register with the city. $6,829.77
4/29/25, Ohio Plumbing & Boiler
Replaced Wilkins 1" 720A Backflow 720A Irrigation backflow preventor that had frozen and split. added a drain valve at the base of the outlet pope for winterization. $1,371.38
4/15/25, All Hours Quote for the same as the above was $1,421.00, so went with IER Services

## Preventative Maint. 2026
MASTER HVAC MAINTENANCE CHECKLIST
Location: 707 Park Meadow Rd
Quotes
All Hours | Never would sent over estimate for 2026, previous vendor. Tammie does not plan on using them in 2026.
Ohio Heating/IER | 8600 | (quarterly filter changes labor and materials not included. Crown will handle this in-house.)
Comfort Systems USA | 6900 | (quarterly filter changes labor and materials not included. Crown will handle this in-house.) | Tammie finalized contract on 4/17/26

## WSHP
Equipment ID | Task | Frequency | Can In-House Do? | Last PM Date | Next Due Date | Status | Notes
| Replace filters | Quarterly | Yes |  |  | In Progress | Tammie has ordered filters, MRS will remove and replace all filters when they arrive.
| Clean return air grilles | Quarterly | Yes |  |  | Not Started | MRS will do when he replaces filters
| Clean accessible condenser coil surfaces | Semi-Annual | Yes |  |  | Not Started | Scheduled for 4/24/26
| Clean condensate pan & flush drain line | Semi-Annual | Yes |  |  | Not Started
| Add condensate pan tablets | Semi-Annual | Yes |  |  | Not Started
| Check for unusual noise/vibration | Semi-Annual | Yes |  |  | Not Started
| Inspect blower belts | Semi-Annual | Yes |  |  | Not Started
| Replace blower belts | Annual | Yes |  |  | Not Started
| Check thermostat operation | Semi-Annual | Yes |  |  | Not Started
| Record supply/return air temperature difference (ΔT) | Semi-Annual | Yes |  |  | Not Started
| Test refrigerant pressures | Semi-Annual | No |  |  | Not Started
| Check entering/leaving water temperatures | Semi-Annual | No |  |  | Not Started
| Inspect water valves and balance | Annual | No |  |  | Not Started
| Inspect electrical components (capacitor, contactor, transformer, board) | Annual | No |  |  | Not Started
| Inspect compressor & reversing valve | Annual | No |  |  | Not Started
Filters Needed | Koch Filters Multi-Pleat XL8 SC 102-700-008 MERV 8 Extended Surface Pleated Panel Filter 20Hx20Lx1W (Pack of 12) HOW MANY NEEDED | [5 empty] | https://www.amazon.com/Koch-Filters-Multi-Pleat-102-700-008-20Hx20Lx1W/dp/B00FFJFRE0
| Koch Filters Multi-Pleat XL8 SC 102-700-021 MERV 8 Extended Surface Pleated Panel Filter 20Hx25Lx2W (Pack of 12) HOW MANY NEEDED | [5 empty] | https://www.amazon.com/Koch-Filters-Multi-Pleat-102-700-021-20Hx25Lx2W/dp/B00FFJGDHU
Koch Fitlers Multi-Pleat or similiar 20HX25LX1W (Pack of 12)
Odd retangle getting current sizes now.

## CoolingTower
Equipment ID | Task | Frequency | Can In-House Do? | Last PM Date | Next Due Date | Status | Notes
| Visual inspection of tower basin | Semi-Annual | Yes |  |  | Not Started | Scheduled for 4/22/26
| Remove debris from screens and louvers | Semi-Annual | Yes |  |  | Not Started
| Clean drift eliminators | Semi-Annual | Yes |  |  | Not Started
| Light rinse of fill media (no chemicals) | Semi-Annual | Yes |  |  | Not Started
| Check make-up water float operation | Semi-Annual | Yes |  |  | Not Started
| Inspect pump strainers (external) | Semi-Annual | Yes |  |  | Not Started
| Inspect visible piping for leaks | Semi-Annual | Yes |  |  | Not Started
| Check fan rotation and listen for abnormal noise | Semi-Annual | Yes |  |  | Not Started
| Check for excessive vibration | Semi-Annual | Yes |  |  | Not Started
| Manage tower water chemical treatment | Semi-Annual | No |  |  | Not Started
| Adjust bleed-off and verify water chemistry | Semi-Annual | No |  |  | Not Started
| Inspect and service fan motor and bearings | Semi-Annual | No |  |  | Not Started
| Inspect and repair structural components (basin, casing, supports) | Semi-Annual | No |  |  | Not Started

## Boiler
Equipment ID | Task | Frequency | Can In-House Do? | Last PM Date | Next Due Date | Status | Notes
| Check water level sight glass | Annual | Yes |  |  | Not Started
| Inspect area around boiler for leaks | Annual | Yes |  |  | Not Started
| Verify combustion air openings are clear | Annual | Yes |  |  | Not Started
| Clean exterior of boiler | Annual | Yes |  |  | Not Started
| Inspect vent area/stack for blockages | Annual | Yes |  |  | Not Started
| Verify thermostat/call-for-heat response | Annual | Yes |  |  | Not Started
| Combustion analysis and tuning | Annual | No |  |  | Not Started
| Clean and inspect burner assembly | Annual | No |  |  | Not Started
| Test and inspect gas valve | Annual | No |  |  | Not Started
| Inspect and clean flame sensor/igniter | Annual | No |  |  | Not Started
| Inspect heat exchanger | Annual | No |  |  | Not Started
| Test relief valve and safety controls | Annual | No |  |  | Not Started
| Test expansion tank and system pressure | Annual | No |  |  | Not Started

## MUA
Equipment ID | Task | Frequency | Can In-House Do? | Last PM Date | Next Due Date | Status | Notes
| Replace filters | Semi-Annual | Yes |  |  | Not Started | Scheduled for 4/24/26
| Clean outside air screens and intake | Semi-Annual | Yes |  |  | Not Started
| Inspect belts and pulleys | Semi-Annual | Yes |  |  | Not Started
| Clean blower wheel and housing (accessible) | Semi-Annual | Yes |  |  | Not Started
| Verify unit starts and stops normally | Semi-Annual | Yes |  |  | Not Started
| Record supply air temperature | Semi-Annual | Yes |  |  | Not Started
| Inspect gas burner and ignition system | Annual | No |  |  | Not Started
| Inspect and test heat exchanger | Annual | No |  |  | Not Started
| Test safeties and high-limit switches | Annual | No |  |  | Not Started
| Inspect electrical wiring and connections | Annual | No |  |  | Not Started

## Pumps
Equipment ID | Task | Frequency | Can In-House Do? | Last PM Date | Next Due Date | Status | Notes
| Visual inspection of pump and surrounding area | Semi-Annual | Yes |  |  | Not Started | Scheduled for 4/24/26
| Check isolation valves for proper position | Semi-Annual | Yes |  |  | Not Started
| Inspect and clean external strainers (if installed) | Semi-Annual | Yes |  |  | Not Started
| Check for vibration and unusual noise | Semi-Annual | Yes |  |  | Not Started
| Inspect pump couplings | Semi-Annual | Yes |  |  | Not Started
| Check for leaks at seals and pipe connections | Semi-Annual | Yes |  |  | Not Started
| Service pump seals and bearings | Annual | No |  |  | Not Started
| Inspect and test pump motor and wiring | Annual | No |  |  | Not Started
| Rebalance and verify system water flow | Annual | No |  |  | Not Started

## ExhaustFans
Equipment ID | Task | Frequency | Can In-House Do? | Last PM Date | Next Due Date | Status | Notes
| Clean fan blades and housing | Annual | Yes |  |  | Not Started | Scheduled for 4/24/26
| Inspect and replace fan belts as needed | Annual | Yes |  |  | Not Started
| Inspect guards/screens and clean | Annual | Yes |  |  | Not Started
| Check for vibration and unusual noise | Annual | Yes |  |  | Not Started
| Verify fan operation (on/off per control) | Annual | Yes |  |  | Not Started
| Inspect motor and electrical connections | Annual | No |  |  | Not Started
| Service fan bearings | Annual | No |  |  | Not Started

## PM_Log
Timestamp (auto) | Tech Name | Date of Visit | Location | Equipment Type | Equipment ID | Task | Status | Notes